## PumpSelection
University of Minnesota Pump Selection Procedure - 10/25/04
All boxed rectangles must be entered, the rest will be calculated.
1. | Determine pump capacity:
A. Gravity Distribution
1. Minimum required discharge is 10 gpm
2. Maximum suggested discharge is 45 gpm
For other establishments at least 10% greater than the water
supply rate, but no faster than the rate at which effluent will flow
out of the distribution device.
B. Pressure Distribution - see pressure design worksheet
| Selected Pump Capacity: |  |  |  | gpm
2. | Determine Total Dynamic Head (TDH)
A. | Elevation difference between pump and point of discharge.
feet
B. | Special head requirement? (See Figure - Special Head Requirements)
|  | feet | [5 empty] | Special Head Requirements
[8 empty] | Gravity Distribution |  | 0ft
C. | Friction loss in supply pipe | [6 empty] | Pressure Distribution |  | 5ft
| 1. Select pipe diameter |  |  | in
2. Enter Figure E-9 with gpm (1A or B) and pipe diameter (C1)
| Read friction loss in feet per 100 feet from Figure E-9 | [6 empty] | E-9 Friction Loss in Plastic Pipe
| Friction loss= |  | ft/ 100 ft of pipe | [5 empty] | per 100 ft
nominal
| 3. Determine total pipe length from pump discharge to soil system discharge point. | [6 empty] | Flow Rate (gpm) |  | pipe diameter
| Estimate by adding 25 percent to pipe length for friction loss in fittings. | [7 empty] | 1.5" | 2.0" | 3"
| Pipe length times 1.25 = equivalent pipe length | [6 empty] | 20 | 2.47 | 0.73 | 0.11
|  | ft x 1.25 = | 0 | feet |  |  |  | 25 | 3.73 | 1.11 | 0.16
[8 empty] | 30 | 5.23 | 1.55 | 0.23
| 4. Calculate total friction loss by multiplying friction loss (C2) | [6 empty] | 35 | 6.96 | 2.06 | 0.3
| by the equivalent pipe length (C3) and divide by 100. | [6 empty] | 40 | 8.91 | 2.64 | 0.39
| Friction Loss = | 0 | ft/100ft X | 0 | ft / 100 = | 0 | feet | 45 | 11.07 | 3.28 | 0.48
[8 empty] | 50 | 13.46 | 3.99 | 0.58
D. | Total head requirement is the sum of elevation difference (A), special | [6 empty] | 55 |  | 4.76 | 0.7
| head requirements (B), and total friction loss (C4). | [6 empty] | 60 |  | 5.6 | 0.82
| 0 | ft + | 0 | ft + | 0 | ft |  | 65 |  | 6.48 | 0.95
[8 empty] | 70 |  | 7.44 | 1.09
| Total Head: |  | 0 | feet
3. | Pump Selection
| 1. A pump must be selected to deliver at least |  |  |  | 0 | gpm (1A or B)
| with at least | 0 | feet of total head (2D).
I hereby certify that I have completed this work in accordance with all applicable ordinances, rules and laws.
|  |  | (signature) |  |  |  | (license #) | ________________(date)